## Routing Decision Tool
Cable Routing Decision Tool with Full Logic
Input Item | Selection / Value
Area | Outdoor | Primary Voltage Category
Primary System Type | Power 400/230V | Shared Voltage Category
Shared With System Type | Speaker 100V | Primary Philosophy
Same Tray Considered | Yes | Shared Philosophy
Separator Applied | Yes | Speaker and Low Signal Conflict
Construction Schedule | Different Phase | Power Involved
Tray Spare Percentage | 20% | Low Signal Involved
Owner Approval Granted? | Yes | Indoor Restriction
Automatic Decision Output | Result
Sharing Allowed
Separator Mandatory
Dedicated Tray Required
Separation Review Required
Construction Schedule Compatible
Tray Spare Status
Typical Route Model
Final Decision Owner
Layout Strategy
Summary
Owner Discussion Notes
Use this area to record project-specific agreements, exceptions, or Owner comments. Any exception to automatic decision output should be approved by the Final Decision Owner.

## Reference Data
Area |  | System Type |  | Same Tray | Separator Applied | Construction Schedule
Outdoor |  | FO Cable |  | Yes | Yes | Same Phase
Indoor |  | Power 400/230V |  | No | No | Different Phase
Control Room |  | Beacon 230V |  |  | Not Applicable
Speaker 100V
Beacon 24-48V
Call Station 24-48V
Analog Tel 24-48V
UTP 5V
Signal under 24V
System Type | Voltage Category | Discipline | Default Sharing Philosophy | Notes
FO Cable | Voltage Independent | Telecom | Generally Shareable | Normally shareable subject to routing and installation protection.
Power 400/230V | 400V or below | Electrical | Limited Sharing | Separator and separation review typically required when sharing.
Beacon 230V | 400V or below | Electrical | Limited Sharing | Treat similar to LV power.
Speaker 100V | 100V or below | Telecom | Normally Separated | Separate from UTP and low level signal systems.
Beacon 24-48V | 60V or below | Instrument | Mostly Not Shareable | Low voltage signal/control category.
Call Station 24-48V | 60V or below | Instrument | Mostly Not Shareable | Low voltage signal/control category.
Analog Tel 24-48V | 60V or below | Telecom | Mostly Not Shareable | Low voltage telecom/signal category.
UTP 5V | 60V or below | Telecom | Mostly Not Shareable | Sensitive data cable. Separate from 100V speaker and power.
Signal under 24V | 60V or below | Instrument | Mostly Not Shareable | Sensitive signal cable. Separate from 100V speaker and power.

## Decision Rules
Cable Routing Decision Logic
Rule | Logic Applied
Area override | Indoor and Control Room are treated as very limited sharing. Sharing is generally rejected unless project-specific approval is granted.
Same tray not considered | If Same Tray Considered is No, use separate tray or trench and separator is Not Applicable.
FO Cable | FO cable is generally shareable, but area and schedule checks still apply.
Power 400/230V or Beacon 230V | Sharing is limited. If same tray is considered, separator and separation review are required.
Speaker 100V | Speaker 100V shall be separated from UTP and low-level signal systems.
UTP or Signal under 24V | UTP and low-level signal systems are mostly not shareable with power or 100V speaker.
Separator check | If separator is mandatory but not applied, sharing is rejected.
Schedule check | If same tray installation is in different construction phases, sharing is rejected for constructability reasons.

## Typical Route Models
Route Code | Area | Typical Route Model | Default Owner | Description
TR-01 | Outdoor | Outdoor Common Route | Common Route Lead | Main outdoor shared route along process unit or pipe rack. Flexible with review.
TR-02 | Outdoor | Roadside Tray or Trench | Common Route Lead | Roadside tray or trench arrangement for inter-area routing.
TR-03 | Indoor | Building Entry Segregated Route | Engineering Manager | Building entry area with controlled separation and limited sharing.
TR-04 | Control Room | Control Room Dedicated Route | Engineering Manager | Dedicated and highly restricted route inside control room.