## Routing Decision Tool
Cable Routing Decision Tool with Full Logic
Input Item | Selection / Value
Area | Outdoor | Primary Voltage Category | 400V or below
Primary System Type | Power 400/230V | Shared Voltage Category | 100V or below
Shared With System Type | Speaker 100V | Primary Philosophy | Limited Sharing
Same Tray Considered | Yes | Shared Philosophy | Normally Separated
Separator Applied | Yes | Speaker and Low Signal Conflict | No
Construction Schedule | Different Phase | Power Involved | Yes
Tray Spare Percentage | 20% | Low Signal Involved | No
|  | Indoor Restriction | No
Automatic Decision Output | Result
Sharing Allowed | No
Separator Mandatory | Yes
Dedicated Tray Required | Yes
Separation Review Required | Yes
Construction Schedule Compatible | No
Typical Route Model | TR-02 Roadside Tray or Trench
Final Decision Owner | Common Route Lead
Decision Summary | Sharing not recommended. Use dedicated tray or trench and confirm final route owner.
Owner Discussion Notes
Use this area to record project-specific agreements, exceptions, or Owner comments. Any exception to automatic decision output should be approved by the Final Decision Owner.

## Reference Data
Area |  | System Type |  | Same Tray | Separator Applied | Construction Schedule
Outdoor |  | FO Cable |  | Yes | Yes | Same Phase
Indoor |  | Power 400/230V |  | No | No | Different Phase
Control Room |  | Beacon 230V |  |  | Not Applicable
Speaker 100V
Beacon 24-48V
Call Station 24-48V
Analog Tel 24-48V
UTP 5V
Signal under 24V
System Type | Voltage Category | Discipline | Default Sharing Philosophy | Notes
FO Cable | Voltage Independent | Telecom | Generally Shareable | Normally shareable subject to routing and installation protection.
Power 400/230V | 400V or below | Electrical | Limited Sharing | Separator and separation review typically required when sharing.
Beacon 230V | 400V or below | Electrical | Limited Sharing | Treat similar to LV power.
Speaker 100V | 100V or below | Telecom | Normally Separated | Separate from UTP and low level signal systems.
Beacon 24-48V | 60V or below | Instrument | Mostly Not Shareable | Low voltage signal/control category.
Call Station 24-48V | 60V or below | Instrument | Mostly Not Shareable | Low voltage signal/control category.
Analog Tel 24-48V | 60V or below | Telecom | Mostly Not Shareable | Low voltage telecom/signal category.
UTP 5V | 60V or below | Telecom | Mostly Not Shareable | Sensitive data cable. Separate from 100V speaker and power.
Signal under 24V | 60V or below | Instrument | Mostly Not Shareable | Sensitive signal cable. Separate from 100V speaker and power.

## Decision Rules
Cable Routing Decision Logic
Rule | Logic Applied
Area override | Indoor and Control Room are treated as very limited sharing. Sharing is generally rejected unless project-specific approval is granted.
Same tray not considered | If Same Tray Considered is No, use separate tray or trench and separator is Not Applicable.
FO Cable | FO cable is generally shareable, but area and schedule checks still apply.
Power 400/230V or Beacon 230V | Sharing is limited. If same tray is considered, separator and separation review are required.
Speaker 100V | Speaker 100V shall be separated from UTP and low-level signal systems.
UTP or Signal under 24V | UTP and low-level signal systems are mostly not shareable with power or 100V speaker.
Separator check | If separator is mandatory but not applied, sharing is rejected.
Schedule check | If same tray installation is in different construction phases, sharing is rejected for constructability reasons.

## Typical Route Models
Route Code | Area | Typical Route Model | Default Owner | Description
TR-01 | Outdoor | Outdoor Common Route | Common Route Lead | Main outdoor shared route along process unit or pipe rack. Flexible with review.
TR-02 | Outdoor | Roadside Tray or Trench | Common Route Lead | Roadside tray or trench arrangement for inter-area routing.
TR-03 | Indoor | Building Entry Segregated Route | Engineering Manager | Building entry area with controlled separation and limited sharing.
TR-04 | Control Room | Control Room Dedicated Route | Engineering Manager | Dedicated and highly restricted route inside control room.